Ata de Reunião/Minute meeting

Data/Date: 18-05-2015

Presenças/ In attendance:

Hugo Brito, atelier Densidades

Andrew Dyson, Capital Constructions

Pedro Marcos, Termoflux

Américo Cabrita, Lux Projects

José Fernandes, Lux Projects

Helder, Deritec

José Dias, Climalgarve

Assuntos tratados:/ Issues discussed:

Climalgarve vai apresentar proposta, mantendo unidades da Mitsubishi em conformidade com a proposta inicial da Penguin. Máquinas de AVAC devem ter ligações à domótica para controlo de ligar/desligar, temperatura, consumo energético

Climalgarve will present proposal, using inital Penguin specifications for Mitsubishi HVAC machines. Machines must have the agreed protocol to communicate with the domotics with control for zones On/Off, temperature sensor and power consumption.

Piso radiante deverá ter ligações à domótica para controlo de ligar/desligar, temperatura, consumo energético

Under Floor Heating must have link to domotics with control for zones, On/Off, temperature sensor and power consumption

Paineis solares com ligação à domótica com sensor de falta de pressão

Solar panels with link to domotics with sensor to inform lack of pressure

Deverá ser contabilizado e alterado no projeto de piso radiante, a zona de circulação ( -1.19 ) e zona de estar ( -1.13 ), junto à piscina interior

Under Floor Heating also to be quoted and installed in areas surrounding interior swimming pool ( Rooms -1.19 and -1.13 )

Piscina exterior, uma vez que têm cobertura elétrica, prever apenas pré-instalação de bomba de calor

Exterior swimming pool to have just pre-instalation for heat pump, since it will have an eletric pool cover

Sistema de paineis solares propostos da marca Junckers/Bosch em vez de Tysun desde que cumpra especificações iniciais da Penguin

Solar panel system to be from Junckers/Bosch instead of Tysun, as long as it complies to the same initial specifications on the Penguin proposal

Bombas na casa das máquinas, verificar quais terão alimentaçao fotovoltaica

Verify which swimming pool pumps will have fotovoltaic panel energy supply. All ideally.

Prever parede dupla com isolamento nos arrumos do dance studio ( compartimento -1.25 ) para evitar condensações nas paredes junto à piscina interior

Walls in dance studio storage ( Room -1.25 ) to have insulation to avoid water condensation on wall near interior swimming pool. Plus walls in indoor pool area to be insulated well to avoid excess wall condensation.

Prioridades de utilização de aquecimento de água, através de válvulas de três vias com controlo pela domótica:

Inverno: 1º Aquas quentes sanitárias, 2º Pavimento radiante, 3º Piscinas

Verão: 1º Águas quentes sanitárias, 2º Piscinas, 3º Pavimento Radiante

Priority of use regarding heating of water, made by three way valve system, controlable by domotics:

Winter: 1st House waters, 2nd Under Floor Heating, 3rd Swimming Pools

Summer: 1st House waters, 2nd Swimming Pools, 3rd Under Floor Heating

An option to priorities which pool to be heated first by the solar panels, should be considered.

Climalgarve will finalise plans with two weeks and present to us and our engineer to check the detail. The ducting already calculated by our engineer should remain the same. Detailed schematics are required for Deritec to plan the control.

It was suggested that UFH needs to be in the indoor pool corridor as this was not included in the Penguin specification.

It is agreed that the HVAC system in the indoor pool must accurately control the air temperate must be carefully monitored to always remain 1ºC higher than the water temperature

It was confirmed by Termoflux that there is no need for a cisterna for the domestic water as the pump can connect directly to the mains water supply which would avoid a total loss of water pressure if the pump failed.

Deritec will be responsible to handle the control elements of the HVAC system with the cooperation of Climalgarve. Climalgarve must ensure that values, sensors and the correct communication protocol is in the machines to provide the base for Deritec to work.

Vanessa Roff Interiors and client need to decide the linear grill style and coving detail. Some rooms have no coving so a liner grill will be visible.